.1	Supply a double wall, factory-built chimney, listed in accordance with UL 103 and ULC/ORD-C959.  All products shall bear the appropriate label.

.2	The chimney shall withstand a continuous operating temperature of up to 540°C (1000°F) and must have been tested at 760°C (1400°F) for 1 hour and 927°C (1700°F) for 10 minutes.

.3	The inner wall shall be made of 20 gauge, type 304 or 316 stainless steel with continuous plasma welds.  Outer wall shall be made of 24 gauge, type 304 or 316 stainless steel.  Two (2) inches of mineral fiber insulation must be included between the inner and outer walls.

.4	All inner pipe joints shall be inserted, held together and sealed using an assembly band and a low temperature sealant (LTS), for flue gas temperatures up to 600°F, or a high temperature sealant (HTS), for flue gas temperatures over 600°F, as supplied by the manufacturer.

.5	All parts, such as appliance adapters, elbows, fittings, expansion joints, tees, supports, roof/wall penetrations and terminations required, shall be listed as the same chimney model and shall be provided by a single manufacturer.

.6	The chimney manufacturer shall provide adapters for fittings, to permit the installation of any required equipment, such as barometric damper, induced fan and test ports.

.7	All exposed galvanized and aluminized steel surfaces shall be at all times protected with a minimum of one base coat primer and one finish coat of heat and corrosion resistant paint (supplied and applied by installer).

.8	The installation must be in accordance with the manufacturer's installation instructions and with the requirements of NFPA-211 and any other local code.